## Schedule 1
Schedule:1 BOQ for 40MW Shaikh Mesri Solar energy absorption through Hamisha Bahar SS
Item | Description of the item | Unit | Qty | Unit Price (AFN) | Total Price (AFN) | ملاحظات
1 | 20KV Indoor Metal Clad Switchgear (as per technical data sheet and PSLD)
1.1 | 20KV indoor enclosed metal clad switchgear for Incomer equiped with: Vacum Circuit breaker(1250A), 25KA/3s, BIL 24/50/125KV. Control, Protection, and Measurement Unit (CPM) comprising: 50/51, 50N/51N, 27/59, 67/67N, Sensitive E/F, Under Frequency,Breaker Failure,TCS, Auto Reclose, ,Ground Sensor,Event Recorder,Fault Recorder and Fault Locator, Mimic Diagram (Ral-1018),Announciation board, Voltmeter with selector switch, Ammeters,Current Transformer (CT), Voltage Transformer (VT), and core blance 50/1A,Earth Switch,Surge arrestor,Power Quality Analyzer (PQA),Earthing Push Button,Local/Remote Selector Switch, PT MCB, Synchronizing Switch ,Lockout Reset and Lamp Test Push Button. Indication Lamps: Spare – white; DC Supply Fail – Red ; O/C & E/F TRIP-Red; O/C & E/F Alarm-Red; Spring charged – Blu; Breaker off-green ; Breaker On-Red ; TCS Fail – Red IF any things missing in mentioned panel, should be added as per standard | set | 4 |  | 0
1.2 | 20KV Indoor enclosed metal clad switchgear for Outgoing equipped with: Vacum Circuit breaker (630A), 25KA/3s, BIL 24/50/125KV. Control, Protection, and Measurement Unit (CPM) comprising: 50/51, 50N/51N, 27/59, 67/67N, Sensitive E/F, Breaker Failure Relays ,Event Recorder,Fault Recorder Auto Reclose, Fault Locator Mimic Diagram (Ral-1018),Announciation board, Voltmeter with selector switch, Ammeters, Lockout relay, TCS ,Current Transformer (CT), Surge arrestor,Earth Switch,Power Quality Analyzer (PQA),Earthing Push Button,Local/Remote Selector Switch, Lockout Reset and Lamp Test Push Button. Indication Lamps: Spare – white; DC Supply Fail – Red; O/C & E/F TRIP-Red; O/C & E/F Alarm-Red; Spring charged – Blue; Breaker off-green; Breaker On-Red; IF any things missing in mentioned panel, should be added as per standard | set | 4 |  | 0
1.3 | 20 kV Indoor enclosed metal clad switchgear, Interconnection feeders old system with new , equipped with: Vacum Circuit breaker(630A), 25KA/3s,BIL 24/50/125KV. Control, Protection, and Measurement Unit (CPM) comprising: 50/51, 50N/51N, 27/59, 67/67N, Sensitive E/F, Breaker Failure Relays ,Event Recorder,Fault Recorder Mimic Diagram (Ral-1018),PQA, Announciation board, Voltmeter with selector switch, Ammeters, Lockout relay, TCS,Lockout relay,Current Transformer (CT),Voltage Transformer (VT),Earth Switch,Earthing Push Button,Local/Remote Selector Switch, Lockout Reset and Lamp ,Trip push button,Test Push Buttons. Indication Lamps: Spare – white; DC Supply Fail – Red; O/C & E/F TRIP-Red; O/C & E/F Alarm-Red; Spring charged – Blue; Breaker off-green; Breaker On-Red IF any things missing in mentioned panel, should be added as per standard | set | 4 |  | 0
1.4 | 20 kV enclosed metal clad switchgear for Bus Coupler system equiped with:20 kV Busbar,Vacuum Circuit Breaker (VCB), 1250 A, 25 kA/3 s, BIL 24/50/125KV, Control, Protection, and Measurement Unit (CPM) comprising:50/51, 50N/51N,27/59,Synchronizing Relay / Synch Check Unit,Breaker Failure Relays,Sensitive E/F ,Event Recorder, Fault Recorder,Mimic Diagram (Ral-1018),Voltmeter with selector switch,TCS , Ammeter Indicator,Announciation board,Current Transformer (CT),Earth Switch,Local/Remote Selector Switch,Close / ON (Green) push Button,Earthing / Grounding Push Button(Blue),Lockout Reset Push Button,Trip Push Button,Lamp Test Push Button. Indication Lamps: Spare – White; DC Supply Fail – Red; O/C & E/F Trip – Red; O/C & E/F Alarm – Red; Spring Charged – Blue; Breaker Off – Green; Breaker On – Red ; IF any things missing in mentioned panel, should be added as per standard | set | 1 |  | 0
1.5 | 20kV Indoor Metal-Clad Switchgear for metering and Bus Riser to new control Room Equipped with: 20kV busbar, VTs, earth switches,Phase indicator ,Voltmeter with selector switch or its equivalent , protection for metering and Bus Riser, Earthing Push Button, Lamp Test Push Button/Block, Spare/Red, PT MCB, DC Supply Fail/Red, ES Open, ES Close | set | 2 |  | 0
2 | MV & LV cables other equipment (as per technical data sheet) |  |  |  | 0
2.1 | Exo-thermic Welding Powder 150grams. | pcs | 20 |  | 0
2.2 | 20kV XLPE Copper cable (12/20(24kV), 1x400mm2 ( as per Standards IEC 60502 ) | M | 350 |  | 0
2.3 | 20kV XLPE Copper cable (12/20(24kv), 1x300mm2 ( as per Standards IEC 60502 ) | M | 420 |  | 0
2.4 | Indoor termination kits with all related accessories | set | 25 |  | 0
2.5 | Outdoor termination kits with all related accessories | set | 25 |  | 0
2.6 | 4x150mm2 Cu Cable, 0.4kV power cables XLPE, betweeen auxilliary to AC switchgear | m | 150 |  | 0 | همکار کیبل
2.7 | 4x16mm2 Cu Cable, 0.4kV power cables XLPE, betweeen AC switchgear to rectifier | m | 150 |  | 0 | همکار کیبل
2.8 | 1x70mm2 Cu Flexible DC cable, XLPE insulated, betwween reactifier and battry bank | m | 150 |  | 0 | همکار کیبل
2.9 | 18x2.5mm2 Cu Control cable | m | 500 |  | 0
2.1 | 4x4 mm2 Cu, 0.4kV power cable, XLPE insulated for switchgear supply | m | 300 |  | 0
2.1 | AC Distribution Panel including busbar MCCB 400A, with 5 outgoing feeders100A, with 20 Nos MCB 20a for outgoing ac accessaries | Set | 1 |  | 0
2.12 | 220V DC Dustribution Panel | Set | 1 |  | 0
2.13 | 12V, 200 AH Lead acid Batteries including interconnections, terminals, and battery racks and other relatd accessories. | Pcs | 20 |  | 0
2.14 | Rectifier Main input 400V, 50Hz Output 220VDC, As per IEC 60146 | Set | 1 |  | 0
2.15 | Bay control units (IEDs) for medium voltage application for incomer to switchgrear room, incomer to existing control room,outgoing direct to customer, bus coupler with synchrocope (V-V, HZ-HZ, SYCH. DEAWABLE & ROTARY) and bus coupler,smart energy meter as per PSLD, schematic and technical data sheet | lot | 1 |  | 0
2.16 | 25mm Copper Bonded Earthing Rod | Pcs | 20 |  | 0
2.17 | Copper annealed soft-drawn (120mm2) | M | 600 |  | 0 | همکار کیبل
2.18 | Earthing conncetors, riser | Pcs | 100 |  | 0
2.19 | Lightning protection Rod (Air terminals,Down conductors,Surge arresters) | set | 1 |  | 0
2.2 | electrical material including (cable trays, cable connectors, cable fixing material, cable bridges, earthing material, post insulators, and fittings, etc.) to complete the installations in every respect. | lot | 1 |  | 0
3 | Supply of Equipment of SCADA for Shiekh Mesri 20KV SWG |  |  |  | 0
3.1 | Ethernet Switch |  |  |  | 0
3.1.1 | Industrial Network Switch | pcs | 2 |  | 0
3.1.2 | OutDoor Fiber PatchCord | pcs | 2 |  | 0
3.1.3 | LAN Cable (CAT-6) | meter | 300 |  | 0
3.2 | Accessories |  |  |  | 0
3.2.1 | Signal Cable | meter | 150 |  | 0
3.2.2 | Cable tie | pcs | 100 |  | 0
3.2.3 | Power Cable | meter | 200 |  | 0
| Grand Total |  |  |  | 0
نوت: با درنظرداشت اینکه جدول اقلام به رویت جدول شرطنامه ترتیب گردیده است، در صورتیکه در ارقام، واحدات و یا مشخصات تفاوتی موجود باشد، جدول های مندرج شرطنامه مدار اعتبار است.

## Schedule 3
40MW Shaikh Mesri Solar energy absorption through Hamisha Bahar SS
Schedule No. 3; Design & other Service
Item | Description of the item | Unit | Qty | Unit Price (AFN) | Total Price (AFN)
1 | Design and other services
1.1 | Electrical engineering includding all required analysis, assessmenrt, design calculations and design drawings, | lot | 1 |  | 0
1.2 | as beuilt drawings & O & M manual | lot | 1 |  | 0
1.3 | project management includding project quality plan, plannning schedulas and reporting | lot | 1 |  | 0
| Grand Total |  |  |  | 0
نوت: با درنظرداشت اینکه جدول اقلام به رویت جدول شرطنامه ترتیب گردیده است، در صورتیکه در ارقام، واحدات و یا مشخصات تفاوتی موجود باشد، جدول های مندرج شرطنامه مدار اعتبار است.

## Schedule 4
40MW Shaikh Mesri Solar energy absorption through Hamisha Bahar SS
Schedule No. 4; Installation and other services
Item | Description of the item | Unit | Qty | Unit Price (AFN) | Total Price (AFN)
Installation and other services
1 | installation of 20kV equipment includding complete earthing, lightining protection system, busbars, cable & wiring works, etc for the folowing
1.1 | installation of 20kV switchgears includding MV/LV cable and all related accessories and integration with existing scada system | lot | 1 |  | 0
1.2 | installation of AC/DC, rectifier and battry bank and all related accessories system | lot | 1 |  | 0
1.3 | installation material (cable connectors, cable fixing material , cable bridges, earthing material, and all related accessories) | lot | 1 |  | 0
2 | installation of earthing with all extention system | lot | 1 |  | 0
3 | test and commissioning | lot | 1 |  | 0
| Grand Total |  |  |  | 0
نوت: با درنظرداشت اینکه جدول اقلام به رویت جدول شرطنامه ترتیب گردیده است، در صورتیکه در ارقام، واحدات و یا مشخصات تفاوتی موجود باشد، جدول های مندرج شرطنامه مدار اعتبار است.

## Schedule 1-2
Schedules of Rates and Prices
Schedule No. 1;
Item | Description of the item | Unit | Qty | Unit Price (AFN) | Total Price (AFN)
1-A | Supply of main equipment of fiber optic (ADSS) cable for sheikh mesri 40MW SPP to Hamesha Bahar SS (Jalalabd), includding installaion & test
1 | ADSS Cable
| 48 cores ADSS Cable | Km | 8.5 |  | 0
| ADSS suspension fitting | pcs | 160 |  | 0
| ADSS Double Tension | pcs | 20 |  | 0
| Outdoor pole mount jointbox | pcs | 7 |  | 0
2 | Fiber Optic & ADSS Accessories |  |  |  | 0
| 48 core LC UPC ODF with pigrails and splicing | pcs | 3 |  | 0
| Patch cords (SC/LC-ST single-mode, 10meter) | pcs | 8 |  | 0
| Pigtails (Factory - polishes, 1.5-meter, matching connector type() | pcs | 10 |  | 0
| HDPE Duct (32/40mm, UV-resistant, matching connector type) | lot | 1 |  | 0
| Lugs | lot | 1 |  | 0
| Cable Tie | lot | 1 |  | 0
3 | installaion & Test |  |  |  | 0
| Installation 48 core ADSS Cable on MV Poles | work | 1 |  | 0
Installation 48 cores outdoor pole mount joint box, OPD with pigtails, patch cords and splicing
Installation 48 cores ADSS from ODF to jointbox outside of the S/S & SPP
| Grand Total |  |  |  | 0
نوت: با درنظرداشت اینکه جدول اقلام به رویت جدول شرطنامه ترتیب گردیده است، در صورتیکه در ارقام، واحدات و یا مشخصات تفاوتی موجود باشد، جدول های مندرج شرطنامه مدار اعتبار است.

## Schedule 5
40MW Shaikh Mesri Solar energy absorption through Hamisha Bahar SS
Schedule No. 5; Price summary
Item | Description of the item | Total Price (AFN)
1 | Plant and mandatory spare parts supplied | 0
2 | design and other services | 0
3 | electrical installation and all related services | 0
| Schedule No. 1 ( scada Accessaries) | 0
| Grand Total of bid price ( Part one and part 2) | 0
نوت: با درنظرداشت اینکه جدول اقلام به رویت جدول شرطنامه ترتیب گردیده است، در صورتیکه در ارقام، واحدات و یا مشخصات تفاوتی موجود باشد، جدول های مندرج شرطنامه مدار اعتبار است.